## SAU
CDC and Ashrae Reopening HVAC Guidlines For Honeywell
Task | Date Completed | Technician | Additional Data to Support TD3:D15ask Completion. Screen shot of schedules, Specification sheet scan, etc.
Add 2 hours to the beginning and end of the occupied schedule to allow for 10 full air exchanges of each building. | 2020-08-12 | MC | Added 2 hours to the beginning and end of all schedules.
Lock all VAV boxes to 100% open to guarantee Air exchanges. This will likely cause temperature over or undershooting | 2020-08-12 | MC | In discussion with Facilities, VAV boxes set to run at maximum air flow regardless of space temperature.
Verify Fan shutdown and freeze stat alarms are functional and an alarm signal is sent out to a technician for immediate response. | 2020-08-12 | MC/SK | All systems tested to ensure poper operation. Freeze Stat and Fan Failure alarms set up for all units, e-mails to Mike and Sean.
Provide support data to show that we are using the best filter application per hvac specifications and provide the filter secification sheet. | 2020-08-14 | SK/JN | Using very efficient MERV-10 Linked filters, MERV-13 filters are 6 to 6 week backlog. Presented info on filters to Todd.
Verify Airflow data that has been presented in the M&V annual Report. | 2020-08-14 | JN | Techs have verified that control settings meet original specifications of ER Report. All OA damper setpoints have been set to original design settings (ER Project).
Verify fresh air settings on classroom unit ventilators are set to maximize exchange and CO2 sensors are working properly. | 2020-08-14 | MC,SK,SL | In discussion with Facilities have set CO2 setpoints to 500PPM and all OA Damper setpoints have been set to original design settings (ER Project).
Verify Air exchangers are operating a maximum exchange. | 2020-08-14 | SK,MC | All air echangers have been verified to be operating correctly and operating at maximum exchange.
Verify that Restroom Exhaust fans are all functional and have new belts. | 2020-08-14 | SK | All exhaust fans have been serviced to ensure motors operable and belts changed.
Clean AHU and RTU coils and condensate pans and disinfect | 2020-08-14 | SK,SL | All RTU and AHU heating and coiling coils have been cleaned. Condensate pans have been cleaned.
Verify Supply and Return ducts are clean and not restricted | 2020-08-14 | SK,SL | AHU and RTU Units have been cleaned internally, do not have access to ducts downstream of RTU or AHU units. No restictions in units or what can be seen from units.

## NLES
CDC and Ashrae Reopening HVAC Guidlines For Honeywell
Task | Date Completed | Technician | Additional Data to Support Task Completion. Screen shot of schedules, Secification sheet scan, etc.
Add 2 hours to the beginning and end of the occupied schedule to allow for 10 full air exchanges of each building. | 2020-08-12 | MC | Added 2 hours to the beginning and end of all schedules.
Lock all VAV boxes to 100% open to guarantee Air exchanges. This will likely cause temperature over or undershooting | 2020-08-12 | MC | In discussion with Facilities, VAV boxes set to run at maximum air flow regardless of space temperature.
Verify Fan shutdown and freeze stat alarms are functional and an alarm signal is sent out to a technician for immediate response. | 2020-08-12 | MC/SK | All systems tested to ensure poper operation. Freeze Stat and Fan Failure alarms set up for all units, e-mails to Mike and Sean.
Provide support data to show that we are using the best filter application per hvac specifications and provide the filter secification sheet. | 2020-08-14 | SK/JN | Using very efficient MERV-10 Linked filters, MERV-13 filters are 6 to 6 week backlog. Presented info on filters to Todd.
Verify Airflow data that has been presented in the M&V annual Report. | 2020-08-14 | JN | Techs have verified that control settings meet original specifications of ER Report. All OA damper setpoints have been set to original design settings (ER Project).
Verify fresh air settings on classroom unit ventilators are set to maximize exchange and CO2 sensors are working properly. | 2020-08-14 | MC,SK,SL | In discussion with Facilities have set CO2 setpoints to 500PPM and all OA Damper setpoints have been set to original design settings (ER Project).
Verify Air exchangers are operating a maximum exchange. | 2020-08-14 | SK,MC | All air echangers have been verified to be operating correctly and operating at maximum exchange.
Verify that Restroom Exhaust fans are all functional and have new belts. | 2020-08-14 | SK | All exhaust fans have been serviced to ensure motors operable and belts changed.
Clean AHU and RTU coils and condensate pans and disinfect | 2020-08-14 | SK,SL | All RTU and AHU heating and coiling coils have been cleaned. Condensate pans have been cleaned.
Verify Supply and Return ducts are clean and not restricted | 2020-08-14 | SK,SL | AHU and RTU Units have been cleaned internally, do not have access to ducts downstream of RTU or AHU units. No restictions in units or what can be seen from units.

## Sutton
CDC and Ashrae Reopening HVAC Guidlines For Honeywell
Task | Date Completed | Technician | Additional Data to Support Task Completion. Screen shot of schedules, Secification sheet scan, etc.
Add 2 hours to the beginning and end of the occupied schedule to allow for 10 full air exchanges of each building. | 2020-08-12 | MC | Added 2 hours to the beginning and end of all schedules.
Lock all VAV boxes to 100% open to guarantee Air exchanges. This will likely cause temperature over or undershooting | 2020-08-12 | MC | In discussion with Facilities, VAV boxes set to run at maximum air flow regardless of space temperature.
Verify Fan shutdown and freeze stat alarms are functional and an alarm signal is sent out to a technician for immediate response. | 2020-08-12 | MC/SK | All systems tested to ensure poper operation. Freeze Stat and Fan Failure alarms set up for all units, e-mails to Mike and Sean.
Provide support data to show that we are using the best filter application per hvac specifications and provide the filter secification sheet. | 2020-08-14 | SK/JN | These air filters have not been changed, anticipate arriving week of August 24th.
Verify Airflow data that has been presented in the M&V annual Report. | 2020-08-14 | JN | Techs have verified that control settings meet original specifications of ER Report. All OA damper setpoints have been set to original design settings (ER Project).
Verify fresh air settings on classroom unit ventilators are set to maximize exchange and CO2 sensors are working properly. | 2020-08-14 | MC,SK,SL | In discussion with Facilities have set CO2 setpoints to 500PPM and all OA Damper setpoints have been set to original design settings (ER Project).
Verify Air exchangers are operating a maximum exchange. | 2020-08-14 | SK,MC | All air echangers have been verified to be operating correctly and operating at maximum exchange.
Verify that Restroom Exhaust fans are all functional and have new belts. | 2020-08-14 | SK | All exhaust fans have been serviced to ensure motors operable and belts changed.
Clean AHU and RTU coils and condensate pans and disinfect | 2020-08-14 | SK,SL | All RTU and AHU heating and coiling coils have been cleaned. Condensate pans have been cleaned.
Verify Supply and Return ducts are clean and not restricted | 2020-08-14 | SK,SL | AHU and RTU Units have been cleaned internally, do not have access to ducts downstream of RTU or AHU units. No restictions in units or what can be seen from units.

## Bradford
CDC and Ashrae Reopening HVAC Guidlines For Honeywell
Task | Date Completed | Technician | Additional Data to Support Task Completion. Screen shot of schedules, Secification sheet scan, etc.
Add 2 hours to the beginning and end of the occupied schedule to allow for 10 full air exchanges of each building. | 2020-08-12 | MC | Added 2 hours to the beginning and end of all schedules.
Lock all VAV boxes to 100% open to guarantee Air exchanges. This will likely cause temperature over or undershooting | 2020-08-12 | MC | In discussion with Facilities, VAV boxes set to run at maximum air flow regardless of space temperature.
Verify Fan shutdown and freeze stat alarms are functional and an alarm signal is sent out to a technician for immediate response. | 2020-08-12 | MC/SK | All systems tested to ensure poper operation. Freeze Stat and Fan Failure alarms set up for all units, e-mails to Mike and Sean.
Provide support data to show that we are using the best filter application per hvac specifications and provide the filter secification sheet. | 2020-08-14 | SK/JN | Using very efficient MERV-10 Linked filters, MERV-13 filters are 6 to 6 week backlog. Presented info on filters to Todd.
Verify Airflow data that has been presented in the M&V annual Report. | 2020-08-14 | JN | Techs have verified that control settings meet original specifications of ER Report. All OA damper setpoints have been set to original design settings (ER Project).
Verify fresh air settings on classroom unit ventilators are set to maximize exchange and CO2 sensors are working properly. | 2020-08-14 | MC,SK,SL | In discussion with Facilities have set CO2 setpoints to 500PPM and all OA Damper setpoints have been set to original design settings (ER Project).
Verify Air exchangers are operating a maximum exchange. | 2020-08-14 | SK,MC | All air echangers have been verified to be operating correctly and operating at maximum exchange.
Verify that Restroom Exhaust fans are all functional and have new belts. | 2020-08-14 | SK | All exhaust fans have been serviced to ensure motors operable and belts changed.
Clean AHU and RTU coils and condensate pans and disinfect | 2020-08-14 | SK,SL | All RTU and AHU heating and coiling coils have been cleaned. Condensate pans have been cleaned.
Verify Supply and Return ducts are clean and not restricted | 2020-08-14 | SK,SL | AHU and RTU Units have been cleaned internally, do not have access to ducts downstream of RTU or AHU units. No restictions in units or what can be seen from units.

## Simonds
CDC and Ashrae Reopening HVAC Guidlines For Honeywell
Task | Date Completed | Technician | Additional Data to Support Task Completion. Screen shot of schedules, Secification sheet scan, etc.
Add 2 hours to the beginning and end of the occupied schedule to allow for 10 full air exchanges of each building. | 2020-08-12 | MC | Added 2 hours to the beginning and end of all schedules.
Lock all VAV boxes to 100% open to guarantee Air exchanges. This will likely cause temperature over or undershooting | 2020-08-12 | MC | In discussion with Facilities, VAV boxes set to run at maximum air flow regardless of space temperature.
Verify Fan shutdown and freeze stat alarms are functional and an alarm signal is sent out to a technician for immediate response. | 2020-08-12 | MC/SK | All systems tested to ensure poper operation. Freeze Stat and Fan Failure alarms set up for all units, e-mails to Mike and Sean.
Provide support data to show that we are using the best filter application per hvac specifications and provide the filter secification sheet. | 2020-08-14 | SK/JN | Using very efficient MERV-10 Linked filters, MERV-13 filters are 6 to 6 week backlog. Presented info on filters to Todd.
Verify Airflow data that has been presented in the M&V annual Report. | 2020-08-14 | JN | Techs have verified that control settings meet original specifications of ER Report. All OA damper setpoints have been set to original design settings (ER Project).
Verify fresh air settings on classroom unit ventilators are set to maximize exchange and CO2 sensors are working properly. | 2020-08-14 | MC,SK,SL | In discussion with Facilities have set CO2 setpoints to 500PPM and all OA Damper setpoints have been set to original design settings (ER Project).
Verify Air exchangers are operating a maximum exchange. | 2020-08-14 | SK,MC | All air echangers have been verified to be operating correctly and operating at maximum exchange.
Verify that Restroom Exhaust fans are all functional and have new belts. | 2020-08-14 | SK | All exhaust fans have been serviced to ensure motors operable and belts changed.
Clean AHU and RTU coils and condensate pans and disinfect | 2020-08-14 | SK,SL | All RTU and AHU heating and coiling coils have been cleaned. Condensate pans have been cleaned.
Verify Supply and Return ducts are clean and not restricted | 2020-08-14 | SK,SL | AHU and RTU Units have been cleaned internally, do not have access to ducts downstream of RTU or AHU units. No restictions in units or what can be seen from units.

## KRHS
CDC and Ashrae Reopening HVAC Guidlines For Honeywell
Task | Date Completed | Technician | Additional Data to Support Task Completion. Screen shot of schedules, Secification sheet scan, etc.
Add 2 hours to the beginning and end of the occupied schedule to allow for 10 full air exchanges of each building. | 2020-08-12 | MC | Added 2 hours to the beginning and end of all schedules.
Lock all VAV boxes to 100% open to guarantee Air exchanges. This will likely cause temperature over or undershooting | 2020-08-12 | MC | In discussion with Facilities, VAV boxes set to run at maximum air flow regardless of space temperature.
Verify Fan shutdown and freeze stat alarms are functional and an alarm signal is sent out to a technician for immediate response. | 2020-08-12 | MC/SK | All systems tested to ensure poper operation. Freeze Stat and Fan Failure alarms set up for all units, e-mails to Mike and Sean.
Provide support data to show that we are using the best filter application per hvac specifications and provide the filter secification sheet. | 2020-08-14 | SK/JN | Using very efficient MERV-10 Linked filters, MERV-13 filters are 6 to 6 week backlog. Presented info on filters to Todd.
Verify Airflow data that has been presented in the M&V annual Report. | 2020-08-14 | JN | Techs have verified that control settings meet original specifications of ER Report. All OA damper setpoints have been set to original design settings (ER Project).
Verify fresh air settings on classroom unit ventilators are set to maximize exchange and CO2 sensors are working properly. | 2020-08-14 | MC,SK,SL | In discussion with Facilities have set CO2 setpoints to 500PPM and all OA Damper setpoints have been set to original design settings (ER Project).
Verify Air exchangers are operating a maximum exchange. | 2020-08-14 | SK,MC | All air echangers have been verified to be operating correctly and operating at maximum exchange.
Verify that Restroom Exhaust fans are all functional and have new belts. | 2020-08-14 | SK | All exhaust fans have been serviced to ensure motors operable and belts changed.
Clean AHU and RTU coils and condensate pans and disinfect | 2020-08-14 | SK,SL | All RTU and AHU heating and coiling coils have been cleaned. Condensate pans have been cleaned.
Verify Supply and Return ducts are clean and not restricted | 2020-08-14 | SK,SL | AHU and RTU Units have been cleaned internally, do not have access to ducts downstream of RTU or AHU units. No restictions in units or what can be seen from units.

## KRMS
CDC and Ashrae Reopening HVAC Guidlines For Honeywell
Task | Date Completed | Technician | Additional Data to Support Task Completion. Screen shot of schedules, Secification sheet scan, etc.
Add 2 hours to the beginning and end of the occupied schedule to allow for 10 full air exchanges of each building. | 2020-08-12 | MC | Added 2 hours to the beginning and end of all schedules.
Lock all VAV boxes to 100% open to guarantee Air exchanges. This will likely cause temperature over or undershooting | 2020-08-12 | MC | In discussion with Facilities, VAV boxes set to run at maximum air flow regardless of space temperature.
Verify Fan shutdown and freeze stat alarms are functional and an alarm signal is sent out to a technician for immediate response. | 2020-08-12 | MC | All systems tested to ensure poper operation. Freeze Stat and Fan Failure alarms set up for all units, e-mails to Mike and Sean.
Provide support data to show that we are using the best filter application per hvac specifications and provide the filter secification sheet. | 2020-08-14 | SK | Using very efficient MERV-10 Linked filters, MERV-13 filters are 6 to 6 week backlog. Presented info on filters to Todd.
Verify Airflow data that has been presented in the M&V annual Report. | 2020-08-14 | JN | Techs have verified that control settings meet original specifications of ER Report. All OA damper setpoints have been set to original design settings (ER Project).
Verify fresh air settings on classroom unit ventilators are set to maximize exchange and CO2 sensors are working properly. | 2020-08-14 | MC,SK,SL | In discussion with Facilities have set CO2 setpoints to 500PPM and all OA Damper setpoints have been set to original design settings (ER Project).
Verify Air exchangers are operating a maximum exchange. | 2020-08-14 | SK,MC | All air echangers have been verified to be operating correctly and operating at maximum exchange.
Verify that Restroom Exhaust fans are all functional and have new belts. | 2020-08-14 | SK | All exhaust fans have been serviced to ensure motors operable and belts changed.
Clean AHU and RTU coils and condensate pans and disinfect | 2020-08-14 | SK,SL | All RTU and AHU heating and coiling coils have been cleaned. Condensate pans have been cleaned.
Verify Supply and Return ducts are clean and not restricted | 2020-08-14 | SK,SL | AHU and RTU Units have been cleaned internally, do not have access to ducts downstream of RTU or AHU units. No restictions in units or what can be seen from units.

## CFM Readings
Acctual Air Exchange Per Building
Building | Building SQFT | Building Ft. Cubed | CFM fresh air based on 10% ASHRARE 2013 Standard | Total CFM Air exchange | CFH | Exchanges per Hour
SAU | 24000 | 192000 | 4225 | 42250 | 2535000 | 13.2031
NLES | 39719 | 317752 | 4250 | 19250 | 1155000 | 3.6349
KRHS | 114000 | 912000 | 18380 | 183800 | 11028000 | 12.0921
KRMS | 123000 | 984000 | 32491 | 320491 | 19229460 | 19.5421
Sutton | 14000 | 112000 | 3125 | 8500 | 510000 | 4.5536
Bradford | 16264 | 130112 | 4975 | 49750 | 2985000 | 22.9418
Simonds | 16466 | 131728 | 6233 | 62330 | 3739800 | 28.3903
0